# SL 71011 CG-S

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire and clear cover = 12,8 m

(mounting height = 6 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 349, H = 188, D = 80

Type: SL 71011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

Manufactured by: CEAG

# SL 71011 CG-S IP54

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side. The electronic part of the luminaire is designed in IP54.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire and clear cover = 13,6 m

(mounting height = 6 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 54

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 350, H = 188, D = 80

Type: SL 71011 CG-S  IP54

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

Manufactured by: CEAG

# RZ  71011 CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: single-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 349, H = 188, D = 80

Type: RZ 71011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

Manufactured by: CEAG

# RZ  71011 CG-S IP54

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side. The electronic part of the luminaire is designed in IP54.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: single-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 54

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 350, H = 188, D = 80

Type: RZ 71011 CG-S  IP54

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wire guard

Manufactured by: CEAG

# RZ  71021 WM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Wall Mounting 90°

Marking: double-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 349, H = 188, D = 80

Type: RZ 71021 WM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- clear cover, structured

- dummy cover

Manufactured by: CEAG

# RZ  71021 DM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Direct ceiling Mounting

Marking: double-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 349, H = 188, D = 80

Type: RZ 71021 DM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- clear cover, structured

- dummy cover

Manufactured by: CEAG

# RZ  71021 PM CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of slim aluminium profile, tarnished anodized with clear cover. Additional light outlet bottom side.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutoff for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Mounting: Pendulum Mounting

Marking: double-sided silk screened legend

Viewing distance: 32 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 40

Colour of enclosure: Aluminium anodized

Inclusive lamp: 8 W T16, 450 Im

Dimensions (mm): L = 349, H = 188, D = 80

Type: RZ 71021 PM CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Pendulum set 0,5 m with canopy , silver

- Pendulum set 1,0 m with canopy , silver

- Pendulum set 1,5 m with canopy , silver

- chain suspension

- clear cover, structured

- dummy cover

Manufactured by: CEAG