SpiritLED 16 CG-S – for recessed ceiling mounting with wire suspension

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with recessed ceiling mounting kit for wire suspension. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Recessed ceiling mounting kit with transparent isolated wire suspension (max.1 m) for voltage supply, chrome plated ceiling duct and plastic housing for the LED converter with strain reliefs for mains and LED-supply.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems.

Different switching modes in one circuit are possible.

Viewing distance:					16 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					II

Type of protection					IP 41/ Converter housing IP 20

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 200; H = 135; T = 20

Dimensions converter housing (mm): 			L = (132 + 85), H = 26, T = 47

(bent shape)

Type: SpiritLED 16 CG-S – for recessed ceiling mounting with wire suspension

Manufactured by: CEAG

SpiritLED 16 CG-S  – for surface ceiling mounting or wall parallel mounting with wire suspension

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with surface mounting kit for wire suspension. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Surface mounting kit for ceiling mounting or wall parallel mounting including with transparent isolated wire suspension (max.1 m) for voltage supply and aluminium coloured canopy.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems. Different switching modes in one circuit are possible.

Viewing distance:					16 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear / aluminium

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					I

Type of protection					IP 41

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 200; H = 135; T = 20

Dimensions canopy (mm): 				W = 200; H = 39; T = 46

Type: SpiritLED 16 CG-S – for surface ceiling mounting or wall parallel mounting with wire suspension

Manufactured by: CEAG

SpiritLED 16 CG-S  – for surface ceiling mounting or wall mounting

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with surface mounting kit. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Surface mounting kit for ceiling mounting or 90° rotated wall mounting including aluminium coloured canopy.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems. Different switching modes in one circuit are possible.

Viewing distance:					16 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear / aluminium Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					I

Type of protection					IP 41

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 200, H = 147, D

Type: SpiritLED 16 CG-S  – for surface ceiling mounting or wall parallel mounting with wire suspension

Manufactured by: CEAG

SpiritLED 28 CG-S– for recessed ceiling mounting with wire suspension

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with recessed ceiling mounting kit for wire suspension. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Recessed ceiling mounting kit with transparent isolated wire suspension (max.1 m)  for voltage supply, chrome plated ceiling duct and plastic housing for the LED converter with strain reliefs for mains and LED-supply.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems.

Different switching modes in one circuit are possible.

Viewing distance:					28 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					II

Type of protection					IP 41/ Converter housing IP 20

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 330; H = 208; T = 20

Dimensions converter housing (mm): 			L = (132 + 85), H = 26, T = 47

(bent shape)

Type: SpiritLED 28 CG-S– for recessed ceiling mounting with wire suspension

Manufactured by: CEAG

SpiritLED 28 CG-S – for surface ceiling mounting or wall parallel mounting with wire suspension

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with surface mounting kit for wire suspension. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Surface mounting kit for ceiling mounting or wall parallel mounting including transparent isolated wire suspension (max.1 m)  for voltage supply and aluminium coloured canopy.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems. Different switching modes in one circuit are possible.

Viewing distance:					28 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear / aluminium

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					I

Type of protection					IP 41

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 330; H = 208; T = 20

Dimensions canopy (mm): 				W = 330; H = 39; T = 46

Type: SpiritLED 28 CG-S– for surface ceiling mounting or wall parallel mounting with wire suspension

Manufactured by: CEAG

SpiritLED 28 CG-S – for surface ceiling mounting or wall mounting

Pos. ...)  ... pcs.

LED – exit sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Exclusive exit sign luminaire with LED technology with surface mounting kit. Frameless optic due to in acrylic integrated legends with LED-module. Uniform illumination of the pictogram by special lightguide technology (Lmin/max >= 0,5).

High service life ensured by optimised LED operating conditions.

Increased safety ensured by redundant construction of the LED unit consisting of three-chip LEDs with high light efficiency > 100 lm/W for distinctly reduced connected load. Reverse polarity protected wiring of the LED unit.

Surface mounting kit for ceiling mounting or 90° rotated wall mounting including with aluminium coloured canopy.

Special LED-Converter with integrated monitoring module for individual monitoring of luminaries (monitoring of the supply and automatic detection of faulty supply of the LED-module).

Switching mode (non-maintained mode, maintained mode or switching maintained mode)

is free programmable with capable emergency lighting systems. Different switching modes in one circuit are possible.

Viewing distance:					28 m

Marking: 						Silk-screened legend

Luminous flux at the end of the rated service time:	100%

Housing material: 					PC, PMMA

Housing colour: 					clear / aluminium

Connection terminal:					clamp terminal 2.5 mm²

Supply voltage:						220 - 240 VAC, 50 Hz  /  176 - 275 VDC

Current consumption - battery operation:		7 mA

Class of protection:					I

Type of protection					IP 41

Permissible ambient temperature: 			-10° Celsius to +40° Celsius

Dimensions panel (mm): 				W = 330; H = 208; T = 20

Dimensions canopy (mm): 				W = 330; H = 39; T = 46

Type: SpiritLED 28 CG-S – for surface ceiling mounting or wall parallel mounting with wire suspension

Manufactured by: CEAG