# 30011 CG-S

Pos. ...)  ... pcs.

Open area/escape route emergency luminaires acc. to EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of sheet steel with mounting clips for clamping range 0 –30mm. With polished aluminium reflector for wide beam distribution:

Max. spacing between luminaire/luminaire = 13.6 m

(mounting height 6m, Emin = 1.25lx, luminous flux at the end of rated service time)

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cut-off for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 40 mA

Power consumption: 17.5 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 mm²

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Lamps (are not part of our delivery content):

for compact fluorescent lamp 10 W (4-pin, TC-DEL), 600 lm

Dimensions (mm): Diameter = 135, Height = 125

Type: 30011 CG-S

Manufactured by: CEAG

# 31011 CG-S

Pos. ...)  ... pcs.

Open area/escape route emergency luminaires acc. to EN 60598-1, EN 60598-2-22 and EN 1838 for recessed mounting.

Enclosure made of sheet steel with mounting clips for clamping range 0 –30mm. With polished aluminium reflector for wide beam distribution:

Max. spacing between luminaire/luminaire = 14.4 m at mounting height 6m and spacing > 11m for mounting height > 2.5m.

(Emin = 1.25lx, luminous flux at the end of rated service time)

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cut-off for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 40 mA

Power consumption: 17.5 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 mm²

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Lamps (are not part of our delivery content):

for compact fluorescent lamp 10 W (4-pin, TC-DEL), 600 lm

Dimensions (mm): Diameter = 195, Height = 145

Type: 31011 CG-S

Manufactured by: CEAG

# 31011 T CG-S (with TC-DEL 10W)

Pos. ...)  ... pcs.

Open area/escape route emergency luminaires acc. to EN 60598-1, EN 60598-2-22 and EN 1838 for recessed mounting.

Enclosure made of sheet steel with mounting clips for clamping range 0 –30mm. With polished aluminium reflector for narrow beam distribution:

Max. spacing between luminaire/luminaire = 13.8 m at mounting height 9 m and spacing > 13m for mounting height  between 7m and 12m.

(Emin = 1.25lx, luminous flux at the end of rated service time)

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cut-off for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 40 mA

Power consumption: 17.5 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 mm²

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Lamps (are not part of our delivery content):

for compact fluorescent lamp 10 W (4-pin, TC-DEL), 600 lm

Dimensions (mm): Diameter = 195, Height = 222

Type: 31011 T CG-S

Manufactured by: CEAG

# 31011 T CG-S (with TC-DEL 13W)

Pos. ...)  ... pcs.

Open area/escape route emergency luminaires acc. to EN 60598-1, EN 60598-2-22 and EN 1838 for recessed mounting.

Enclosure made of sheet steel with mounting clips for clamping range 0 –30mm. With polished aluminium reflector for narrow beam distribution:

Max. spacing between luminaire/luminaire = 17 m at mounting height 14 m and spacing > 16m for mounting height  between 10m and 16m.

(Emin = 1.25lx, luminous flux at the end of rated service time)

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cut-off for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 50 mA

Power consumption: 25 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 mm²

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Lamps (are not part of our delivery content):

for compact fluorescent lamp 13 W (4-pin, TC-DEL), 900 lm

Dimensions (mm): Diameter = 195, Height = 222

Type: 31011 T CG-S

Manufactured by: CEAG