# SL 8011 CG-S

Pos. ...)  ... pcs.

Recessed Ceiling Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of sheet steel, bezel painted with colour RAL 9010. Structured plastic cover. For ceiling thickness up to 40 mm

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutout for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire and clear cover= 15.4 m

(mounting height = 7 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V +10/-15 % 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Inclusive lamp: 8 W T16, 450 lm

Dimensions (mm): L = 360, H = 127, D = 105

Type: SL 8011 CG-S

Manufactured by: CEAG

# SL 8011 CG-S

Pos. ...)  ... pcs.

Recessed Ceiling Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of sheet steel, bezel painted with colour RAL 9010. Structured plastic cover. For ceiling thickness up to 40 mm.

EVG with ENEC-test mark, certified from an independent testing lab. Automatic cutout for failures within the lamp circuit.

Max. spacing between luminaire/luminaire and clear cover= 15.4 m

(mounting height = 7 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 20

Colour of enclosure: White

Inclusive lamp: 8 W T16, 450 lm

Dimensions (mm): L = 360, H = 127, D = 105

Type: SL 8011

Manufactured by: CEAG