# SL 3301 CG-S

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of plastic for ceiling- or recessed ceiling installation. Easy- assembly and relamping.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutout for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Max. spacing between luminaire/luminaire = 13.6 m

(mounting height = 5 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Permissible temperature range: -10°C up to +40°C

Current drawn (battery operation): 40 mA

Power consumption: 17,5 VA

Loop terminals: 2 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 20

Colour of enclosure: White

Lamps (are not part of our delivery content):

For compact fluorescent lamps 10 and 13 W TC-DEL, socket G24-q1

Dimensions (mm): Diameter = 115, Height = 60

Diameter for ceiling installation(mm) = 132

Pos. ...)  ... pcs.

Accessories:

- Ceiling tube for ceiling installation

- Bezel white, chrome colour or brass colour

Type: SL 3301 CG-S

Manufactured by: CEAG

# RZ 3301 CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Enclosure made of plastic for ceiling- or recessed ceiling installation. Easy- assembly and relamping.

Exit cube made of sheet steel incl. 3 legend covers and 1 dummy.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses. Automatic cutout for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: Silk-screened legend

Viewing distance: 40 m

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Permissible temperature range: -10 °C up to +40 °C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II; Degree of protection: IP 20

Dimensions (mm): Diameter = 115, H = 60

Diameter for ceiling installation (mm) = 132

Dimensions of exit cube (mm): W = 242, H = 227, D = 242

Colour of enclosure: White

Lamps (are not part of our delivery content):

For compact fluorescent lamps 10 and 13 W TC-DEL, socket G24-q1

Pos. ...)  ... pcs.

Accessories:

- Ceiling tube for ceiling installation

Type: 3301 CG-S inclusive exit cube

# Manufactured by: CEAG