# 91.1 CG-S

Pos. ...)  ... pcs.

Stair Riser Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Aluminium die-casting enclosure for recessed wall mounting with opaque plastic cover or black grit cover.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses.

Automatic cutout for failures within the lamp circuit.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Voltage range: 230V 50/60 Hz, 220 V DC +25/-20%

Current drawn (battery operation): 20 mA

Power consumption: 10 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: I; Degree of protection: IP 54

Colour of enclosure: White/black

Inclusive lamp: 4 W T16

Dimensions (mm): L = 235, H = 100, D = 82

Type: 91.1 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- opaque plastic cover

- black grit cover

- concrete installation box

- cavity assemble set

- cover with legends PL, PR or PU

Manufactured by: CEAG