CGLine PC-Interface

Pos.   )		Pcs.

CGLine PC-Interface for central control and monitoring of up to 400 pcs. CGLine self contained luminaires, split into 4 lines with up to 100 pcs. Luminaires each, in installations according to EN 50172, DIN VDE 010-718 and DIN V VDE V 0108-100.

All of the data and commands are transmitted via 2-core bus cables. An integrated WEB-server allows a comfortable control and monitoring on any PC workplaces in the intranet (LAN) with an usual WEB-browser, without any further special software. The integrated mail-client allows an comfortable mail notification, depending on selectable events with confirmation requirement, and a second recipient group.

An integrated ping-function allows an automatic detection and visualisation of all installed CGLine PC-interfaces. The visualisation shows data like destination, IP-address, MAC-address and the actual status of each interfaces. The integrated hyperlink-function enables an easy menu guide to the WEB-server.

It is possible to connect up to 8 pcs. CGLine PC-interfaces to an optional available CGVision visualisation software, with up to 3.200 pcs. CGLine self contained luminaires. An optional available licence for a building layout programming, enables a visualisation of all luminaires of a line in one building layout picture, which can be has the typical Auto-CAD format .dxf or .dwg. Layer are free selectable ON or OFF. The luminaires can be selectable in their size and in their type as EXIT sign (green) or safety luminaire (yellow).

Functions:

- Integrated WEB-server for visualisation via usually WEB-browser (e.g. Internet Explorer, Firefox...)

- Mail-Client for up to 10 mail recipients.

- Status of all installed interfaces in the network visible, due to intelligent PING function.

- Up to 8 CGLine PC-Interfaces with up to 3.200 CGLine luminaires on CGVision possible

- Block input with differential-loop monitoring (1 kOhm)

- Automatic luminaire search function (no manual addressing needed)

- Automatic function test, testing distance can be freely selected

- Automatic operating duration test, testing distance can be freely selected

- Split battery duration test: DT of even / uneven addresses are shifted for 24h

- Start / Cancel operating duration test manually

- Block the emergency lighting function (complete or by bus line)

- Luminaires in maintained mode a switchable OFF ( to non-maintained light, complete or each line)

- Display of the luminaire status (Switched ON/OFF)

- constant charge monitoring

- communication monitoring each luminaire / line / interface

- recording the single fault messages

- free entry of luminaire target destination names, each with 20 characters and abbreviated address

assignment via keyboard or by user-friendly PC software

- freely programmable potential-free alarm contact for battery operation, function test, operating

duration test, communication fault, luminaire fault or charging fault.

- LED displays: operation, test and fault

- password protection

- removable configuration and test book memory via memory card for a period of at least 2 years

- evaluation of the test book on memory card using optional card reader and CEAG software on a  
   standard PC

- pre-programming of the configuration memory on the PC

Technical data:

Ethernet port:					1 x RJ45 (LAN)

CGLine connection:			4 x lines (2-core each) with up to 100 CGLine luminaires each

Supply voltage: 				230V AC or 24V DC

Power consumption:			< 4 Watt

Connection terminals: 		2.5 mm²

Ambient temperature:			0...35°C

Degree of protection: 			IP20

Housing:							DIN-rail 10 TE, for built in mounting

Dimensions (mm): 				L=175mm, W=126. D=60

Alarm relay contact:			 1 x UM, 24 V 0.5A; freely programmable

Block input:						S1/S2 with differential loop monitoring, 1kOhm

LED displays: 		Power, sum failure, SD card, status, LAN connection (link),             CGLine (Tx/Rx)

Options:

... pcs. CGLine PC-Interface connection box for wall mounting with cable entries

... pcs. SD-card, formatted for CGLine PC-Interface

... pcs. card-reader for SD memory card

... pcs. CEAG PC Software CGLine 400 for configuration and test book evaluation

Type: CGLine PC-Interface

Manufactured by: CEAG