48011 1-3/D LED CGLine IP41

Pos.    )		Pcs.

Self-monitoring self-contained aluminium LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down 
- generally suitable for maintained or non-maintained mode

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light:							0°C to +35°C

Housing:

Modular luminaire with sturdy aluminium housing and one-sided, rounded cover made of 850 °C glow-wire resistant polycarbonate.

Insulation class: I; degree of protection: IP 41

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 345, H = 200, D = 80

Housing colour: light grey, RAL 7035

Plastic cover:

..... cover with legend (screen printing), viewing distance: 32 m

Accessories:

..... pcs. wire guard

Type: 48011 1-3/D LED CGLine IP41

Manufactured by: CEAG

48011 1-3/D LED CGLine IP54

Pos.    )		Pcs.

Self-monitoring self-contained aluminium LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down 
- generally suitable for maintained or non-maintained mode

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light:							0°C to +35°C

Housing:

Modular luminaire with sturdy aluminium housing and one-sided, rounded cover made of 850 °C glow-wire resistant polycarbonate.

Insulation class: I; degree of protection: IP 54

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 345. H = 200. D = 80

Housing colour: light grey, RAL 7035

Plastic cover:

..... clear cover

..... cover with legend (screen printing), viewing distance: 32 m

Accessories:

..... pcs. wire guard

Type: 48011 1-3/D LED CGLine IP54

Manufactured by: CEAG