1883 1-3/D CGLine

Pos.    )		Pcs.

Self-monitoring self-contained edge lit LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100  for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

- generally suitable for maintained or non-maintained mode

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light:							0°C to +35°C

Housing:

Edge luminaire for recessed ceiling installation including device for easy lamp changing and plastic ceiling bezel in white, RAL 9010.

Insulation class: I; degree of protection: IP 20

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Panel dimensions (mm): W = 242  H = 128

Bezel dimensions (mm): L = 340  W = 100

Ceiling cut-out dimensions (mm): L = 327  W = 75

Minimum installation height (mm): 120

Panel:

- With one-sided legend panel (screen printing), viewing distance: 20m

- With two-sided legend panel (screen printing), viewing distance: 20m

Accessories:

..... pcs. concrete installation box for 1886

..... pcs. installation kit for concrete installation box for 1886

Type: 1883 1-3/D CGLine

Manufactured by: CEAG

1884 1-3/D CGLine

Pos.    )		Pcs.

Self-monitoring self-contained edge lit LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100  for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

- generally suitable for maintained or non-maintained mode

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light:							0°C to +35°C

Housing:

Edge luminaire for recessed ceiling installation including device for easy lamp changing and plastic ceiling bezel in white.

Insulation class: I; degree of protection: IP 20

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Panel dimensions (mm): W = 320  H = 190

Bezel dimensions (mm): L = 400  W = 100

Ceiling cut-out dimensions (mm): L = 387  W = 75

Minimum installation height (mm): 120

Panel:

- With one-sided legend panel (screen printing), viewing distance: 28m

- With two-sided legend panel (screen printing), viewing distance: 28m

Accessories:

..... pcs. concrete installation box for 1884

..... pcs. installation kit for concrete installation box for 1884

Type: 1884 1-3/D CGLine

Manufactured by: CEAG

1984 1-3/D CGLine

Self-monitoring self-contained edge lit LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838 for systems according to EN 50172, DIN VDE 0100-718 and E DIN VDE 0108-100  for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

- generally suitable for maintained or non-maintained mode

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light:							0°C to +35°C

Housing:

Edge luminaire for ceiling installation in sheet steel housing white, RAL 9010.

Insulation class: I; degree of protection: IP 20

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Panel dimensions (mm): W = 320. H = 190

Housing dimensions (mm): L = 361. H = 120. D = 86

Panel:

- With one-sided legend panel (screen printing), viewing distance: 28m

- With two-sided legend panel (screen printing), viewing distance: 28m

Accessories:

..... pcs. pair of pendants 0.5 m

..... pcs. bracket

..... pcs. parallel wall fixing

..... pcs. chain fixing

Type: 1984 1-3/D CGLine

Manufactured by: CEAG