71811 1-3/D LED CGLine

Pos.    )		Pcs.

Self-monitoring self-contained LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838

for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100  for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											4 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 4,8V/1,1Ah

Housing:

Extruded aluminium profile, with mitre cut.

With one-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. wire guard

Type: 71811 1-3/D LED CGLine

Manufactured by: CEAG

71821 1-3/D LED CGLine WM

Pos.    )		Pcs.

Self-monitoring self-contained LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838

for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											8 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 7,2V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light: 							0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut. For wall mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. mounting kit for wall and ceiling mounting

Type: 71821 1-3/D LED CGLine WM

Manufactured by: CEAG

71821 1-3/D LED CGLine DM

Pos.    )		Pcs.

Self-monitoring self-contained LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838

for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											8 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 7,2V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light: 							0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

For ceiling mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. mounting kit for wall and ceiling mounting

Type: 71821 1-3/D LED CGLine DM

Manufactured by: CEAG

71821 1-3/D LED CGLine PM

Pos.    )		Pcs.

Self-monitoring self-contained LED luminaire according to EN 60598-1, EN 60598-2-22 and EN 1838

for systems according to EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation and for connection to the central monitoring device CG-Controller CGLine 400  or the CGLine PC-Interface.

If connected to the central monitoring device CG-Controller CGLine 400 or the CGLine PC-Interface

a non-screened 2-core bus cable to the luminaire is also needed.

Features:

- manual function test or duration test with test button

- selectable operating time 1h or 3h

- brightness selectable in 3 steps

- Test results with fault analysis (lamps, charging and battery circuit) as well as status displays (operation, function test, duration test) via 3 coloured LEDs

- automatic function test (weekly)

- automatic duration test (every 3 months)

- automatic charging monitoring

- deep discharge protection with restart inhibit

- no-load and short-circuit shut down, error prompt in case of breakdown of more then 1 LED

- 1 minute delay of normal mode after mains returns 
- blocking function with CG-Controller CGLine 400 or PC-Interface in times of shut-down

Luminous flux E/N approx. 				50 % at 1h

20 % at 3h

Lamp: 											8 * 1W Power LED

Emergency lighting rated operating time:	1h or 3h

Rechargeable battery:							NiMh 7,2V/1,1Ah

Permitted temperature range:

Maintained light: 								-5°C to + 30°C

Non-maintained light: 							0°C to +35°C

Housing:

Extruded aluminium profile, with mitre cut.

For pendulum mounting.

With two-sided light exit and additional light exit at the bottom.

Lamps can be changed without tools.

Insulation class: II; Degree of protection: IP 40

Connection terminals: 2.5 sq mm

Supply voltage: 230V 50Hz

Dimensions (mm): L = 349 H = 188 D = 80

Housing colour: aluminium matt anodised

Plastic cover:

..... blind cover

..... cover with legend (screen printing), viewing distance: 32 m

Luminaires are generally suitable for maintained or non-maintained mode.

Accessories:

..... pcs. pendulum mounting set 0.5m

..... pcs. pendulum mounting set 1.0m

..... pcs. pendulum mounting set 1.5m

..... pcs. chain fastening

Type: 71821 1-3/D LED CGLine PM

Manufactured by: CEAG