CEAG ZB 96 
Central battery system

Central Battery System ZB96 for supplying power to 220 V AC/DC emergency luminaries in accordance with DIN VDE 0108 dated 10/89, DIN VDE 510 part 2, BGV A2 (VBG4) with individual luminaire monitoring.

Failure detection on each individual emergency luminaire in conjunction with CEAG electronic ballasts including 2L CG monitoring module without additional data cable.

Electronic assemblies of modular, easy to service design

l	Straightforward connections using 2.5 mm2 terminals on plug-in terminal blocks

l	Easy to install and replace due to quick-fixing devices

Large connection space, meets health and safety regulations, plug-in terminals accessible from above or below protected against inadvertent physical contact in accordance with DIN VDE 0100. With built-in terminal strip for the outputs for the battery and mains supply cables to substations including fuse protection.

Microprocessor control module ST20

lDisplay of operating states and luminaire failures on 4-line display

lIntegrated log book memory

lDB25 Centronics interface for the connection of a commercially available printer

lIntegrated remote switching facility via two contacts

lElectronically controlled 24V outputs forvoltage monitoring as many subdistribution boards for the   general lighting system as required in conjunction with 3 three-phase monitoring

lLED indicator for power, mains failure, battery operation, group failure

lPotential-free contacts, power, battery operation, group failure

lStraightforward programming using three keys, can be programmed as standard:

l- Manual reset

l- Delay-time on mains return 1-15 minutes

Charging device

l	Microprocessor-controlled charging 
(IU characteristic)

l	Temperature based with automatic boost charging circuit

l	Temperature sensor built into battery cabinet

l	Design as switched primary, switched-mode regulator

l	Patented charging monitoring method for the detection of open battery circuits

l	With insulation test device

l	Depending on battery size with boost charging unit with electrical isolation

l	LED indications for charging module on, boost charging on, indication of battery capacity > 10 %, > 50 %, 100 %, insulation fault, charging failure, mains present

l	Potential-free contact charging failure, boost charging, insulation fault

Variable module assemblies:

Phase selector module 20 A or 80 A

l	Electronically controlled for switching over to an intact phase on the failure of one or two phases

l	Built into central battery cabinet

Circuit modules

l	Individual switch over per emergency lighting circuit with free programming for maintained or non-maintained mode and two-pole fuse protection in accordance with VDE.

l	Fuses easily accessible on the front of module

l	Electronically isolated mains monitoring for maintained and non-maintained modes

l	LED indicators for failure and power/ON

Maintained light switch monitoring DLS

l	Common switching of general and emergency luminaries during mains operation using existing light switches

l	Freely programmable allocation of max. 2 independent light switches per emergency lighting circuit

l	With 8 switch inputs

l	LED indications failure, switch state on

Staircase light switching module TLS

l	Timer-controlled switching on/off of emergency lighting circuits during mains and battery operation using illuminated buttons

l	Power supply for glow lamps, max. 50 mA per TLS input

l	With 8 button circuit inputs

l	Variable on time from 1 to 15 minutes

l	Freely programmable allocation of buttons/emergency lighting circuits.

l	General and emergency luminaries can be controlled with the same button by using a TLS switching module (installed in the lighting distribution system)

Selective emergency lighting switch on SDS 8

l	Selective switching on of the emergency lighting in the areas affected by the mains failure

l	8 pcs 24V current loops for monitoring subdistribution boards for the general lighting systems in conjunction with 3-three-phase monitoring

l	8 pcs. LED indicators mains failure

4-needle event printer PD2

l	Logging and storage of operating states on a ZB96 installation or US96 substation

l	Event type and period for the print out can be selected using a menu

Relay module CG IV

Relay module for signalling the following

operating states using potential-free contacts:

Emergency/mains operation, emergency

lighting/charging failure, deep discharge

protection, function test on/off, operating time

test on/off

l	8 pcs. LED indicators for indications given above

LON module for the integration of the emergency lighting in building automation

l	Transceiver: FTT10A, 2-wire connection

l	Output data, e.g., installation blocked, deep discharge protection, battery open circuit, battery voltage, current and temperature, insulation fault, booster failure, charging module failure, LON bus error, mains failure, residual capacity, circuit failures...

l	Input commands, e.g., start and cancel function test and operating time test, block and enable manual reset, activate DLS via switch

220V OGi battery block

l	Maintenance-free, sealed and leak-proof

l	Sulphuric acid bound in fabric

l	Extremely low gassing

l	Acid density between 1.24 kg/I and 1.26 kg/I

l	Service life longer than 10 years at 20 °C

l	Low self-discharge

l	Design in accordance with DIN

l	Electrolyte and atmospheric oxygen-proof pole feed-throughs

ZB 96/200

..... pcs. ZB 96/200 – central battery system with automatic test device in accordance with VDE 0108 part 1, 6.4.3.10 and individual luminaire monitoring with CEAG electronic ballasts and 2LCG monitoring module

Rated operating time:	.... h

Recharging cycle:	.... h

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Charging device with microprocessor-controlled, temperature-based charging

Steel sheet cabinet with viewing door.

Degree of protection: electronics cabinet IP 21,

Cable feed from above or below

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 400 mm

For fitting max.18 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. phase selector module 20 A or 80 A

..... pcs. built-in 4-needle event printer PD2

..... pcs. CGP built-in

..... pcs. terminal strip with 4 fuse-protected battery and mains outputs to substations

..... pcs. OGiV battery block  .... Ah

..... pcs. battery cabinet, 
H x B x D: 2050 x 800 x 400 mm

..... pcs. battery support

Type: ZB 96/200

Manufactured by: CEAG

ZB 96/200 S

..... pcs. ZB 96/200S – central battery system with automatic test device in accordance with VDE 0108 part 1, 6.4.3.10 and individual luminaire monitoring with CEAG electronic ballasts and 2LCG monitoring module

Rated operating time:	.... h

Recharging cycle:	.... h

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Charging device with microprocessor-controlled, temperature-based charging

Steel sheet cabinet with viewing door.

Degree of protection: electronics cabinet IP 21,

Cable feed from above or below

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 400 mm

For fitting max. 26 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. phase selector module 20 A or 80 A

..... pcs. built-in 4-needle event printer PD2

..... pcs. terminal strip with 4 fuse-protected battery and mains outputs to substations

..... pcs. OGiV battery block  .... Ah

..... pcs. battery cabinet, 
H x B x D: 2050 x 800 x 400 mm

..... pcs. battery support

Type: ZB 96/200 S

Manufactured by: CEAG

ZB 96/LAD

..... pcs. ZB 96/LAD charging device in accor-dance with DIN VDE 0108/10.89, DIN VDE 0510 part 2 and health and emergency regulations (VBG4) designed for:

..... Ah OGiV battery block

..... h rated operating time

..... h recharging cycle

Comprising:

Steel sheet cabinet with large viewing door.

Degree of protection: IP 21

Cable feed from above or below

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 400 mm

Microprocessor control module and insulation test device

Charging device with microprocessor-controlled, temperature-based charging

Built-in terminal strip with ..... (8/16) fuse protected battery and mains outputs to substations

..... pcs. boost charging unit

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. phase selector module 20 A or 80 A

Type: ZB 96/LAD

Manufactured by: CEAG

ZB 96/260 C

..... pcs. ZB 96/260C – central battery system with automatic test device in accordance with VDE 0108 part 1, 6.4.3.10 and individual luminaire monitoring with CEAG electronic ballasts and 2LCG monitoring module

Rated operating time:	.... h

Recharging cycle:	.... h

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Charging device with microprocessor-controlled, temperature-based charging

Steel sheet cabinet (separated 
electronic and battery cabinet) with viewing door.

Degree of protection: electronics cabinet IP 21,

Battery cabinet IP 21 
Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 600 mm

For fitting max.10 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. phase selector module 20 A

..... pcs. built-in 4-needle event printer PD2

..... pcs. terminal strip with 2 fuse-protected battery and mains outputs to substations

..... pcs. OGiV battery block  .... Ah

Type: ZB 96/260C

Manufactured by: CEAG

ZB 96/200 C

..... pcs. ZB 96/200C - central battery system with automatic test device in accordance with VDE 0108 part 1, 6.4.3.10 and individual luminaire monitoring with CEAG electronic ballasts and 2LCG monitoring module

Rated operating time:	.... h

Recharging cycle:	.... h

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Charging device with microprocessor-controlled, temperature-based charging

Steel sheet cabinet (separated 
electronic and battery cabinet) with viewing door.

Degree of protection: electronics cabinet IP 21,

Battery cabinet IP 21 
Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 400 mm

For fitting max.10 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. phase selector module 20 A

..... pcs. built-in 4-needle event printer PD2

..... pcs. terminal strip with 2 fuse-protected battery and mains outputs to substations

..... pcs. OGiV battery block  .... Ah

Type: ZB 96/200C

Manufactured by: CEAG

ZB 96/160 C

..... pcs. ZB 96/160C - central battery system with automatic test device in accordance with VDE 0108 part 1, 6.4.3.10 and individual luminaire monitoring with CEAG electronic ballasts and 2LCG monitoring module

Rated operating time:	.... h

Recharging cycle:	.... h

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Charging device with microprocessor-controlled, temperature-based charging

Steel sheet cabinet (separated 
electronic and battery cabinet) with viewing door.

Degree of protection: electronics cabinet IP 21,

Battery cabinet IP 21 
Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 1600 mm, W = 600 mm, D = 250 mm

For fitting max.10 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. phase selector module 20 A

..... pcs. built-in 4-needle event printer PD2

..... pcs. terminal strip with 2 fuse-protected battery and mains outputs to substations

..... pcs. OGiV battery block  .... Ah

Type: ZB 96/160C

Manufactured by: CEAG

US 96/200

..... pcs. US 96/200 substation

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet cabinet with viewing door.

Degree of protection: electronics cabinet IP 21,

Cable feed from above or below

Exterior finish: RAL 7035

Dimensions: 
H = 2050 mm, W = 800 mm, D = 400 mm

For fitting max. 26 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: ZB 96/200

Manufactured by: CEAG

US 96/120

..... pcs. US 96/120 substation

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet wall cabinet.

Degree of protection: IP 54,

Cable feed from above

Every output wired to terminals

Exterior finish: RAL 7035

Dimensions: 
H = 1200 mm, W = 600 mm, D = 300 mm

For fitting max. 17 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: ZB 96/120

Manufactured by: CEAG

US 96/80

..... pcs. US 96/80 substation

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet wall cabinet.

Degree of protection: IP 54,

Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 800 mm, W = 600 mm, D = 250 mm

For fitting max. 17 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: ZB 96/80

Manufactured by: CEAG

US 96/85 E 30

..... pcs. US 96/85 - E30 substation with 
30 minute function retention. Tested by an officially approved materials test institute, based on DIN 4012 part 2

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet cabinet for wall mounting.

Degree of protection: IP 54,

Cable feed from above

Exterior finish: RAL 7035

Dimensions cabinet:

H = 850 mm, W = 850 mm, D = 300 mm

Cabinet dimensions incl. fixing elements and cable entries:

H = 950 mm, W = 920 mm, D = 300 mm

For fitting max. 17 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: ZB 96/85 E30

Manufactured by: CEAG

US 96/110 E 30

..... pcs. US 96/110 - E30 substation with 30 minute function retention. Tested by an officially approved materials test institute, based on DIN 4012 part 2

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet cabinet for wall mounting.

Degree of protection: IP 54,

Cable feed from above

Exterior finish: RAL 7035

Dimensions cabinet:

H = 1100 mm, W = 450 mm, D = 400 mm

Cabinet dimensions incl. fixing elements and cable entries:

H = 1200 mm, W = 480 mm, D = 400 mm

For fitting max. 9 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: ZB 96/110 E30

Manufactured by: CEAG

US 96/60

..... pcs. US 96/60 substation

Comprising:

Microprocessor control module with DB25 Centronics printer interface

Steel sheet wall cabinet.

Degree of protection: IP 54,

Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 600 mm, W = 380 mm, D = 210 mm

For fitting max. 5 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

..... pcs. CG IV relay module for signalling operating states and remote switching of function test and operating time test

..... pcs. LON module for interfacing to LON building management systems

..... pcs. built-in 4-needle event printer PD2

..... pcs. built-in AC-module for power supply of the internal electronic in case of battery cable cut

Type: US 96/60

Manufactured by: CEAG

US 96/38

..... pcs. US 96/38 substation

Comprising:

Microprocessor control module ST8

Steel sheet wall cabinet.

Degree of protection: IP 54,

Cable feed from above

Exterior finish: RAL 7035

Dimensions: 
H = 380 mm, W = 380 mm, D = 210 mm

For fitting max. 3 variable modules

Fitted with:

..... pcs. freely programmable final circuits 1A

..... pcs. freely programmable final circuits 2A

..... pcs. freely programmable final circuits 6A

..... pcs. DLS maintained light switch monitoring for the common switching of emergency lighting and general lighting. With 8 switch inputs.

..... pcs. TLS staircase light switch monitoring for timer-controlled switching on/off of emergency lighting circuits during mains and battery operation. With 8 button circuit inputs

..... pcs. SDS 8, 24V current loops, 8-off, for selectively switching on the emergency lighting in conjunction with 3-phase monitoring

Type: US 96/38

Manufactured by: CEAG

Programming and instruction

..... pcs. programming and instruction by 
CEAG customer service following completion of commissioning by the installer.

The basic device functions are programmed (no programming of location data for the luminaires) and instruction of the personnel on using the device.

Inspection contract

..... pcs. Iinspection contract for the emergency lighting.

This inspection contract includes an annual test in accordance with DIN VDE 0108 and covers the following tasks:

l	Mains/emergency lighting switch over function for the devices

l	Visual inspection of the electrical components and the battery in the devices

l	Mechanical inspection of the devices

l	Inspection and adjustment of charging current and charging current regulation

l	Functional test of other electronics

l	Testing of the lamps only on luminaries with CG monitoring

l	Rated operating time test (capacity test) on the accumulators

The replacement of faulty components in the installation or faulty lamps is not included in the inspection!