2L-CG-S

Monitoring module with address-switches for 20 addresses in flame retardant polycarbonate enclosure to UL 94-VO. To be installed in protection class I and II lumin-aires. For function monitoring of loads between 4 - 150 W  (fluorescent lamps with high fre-quency electronic ballast, tungsten halogen lamps with electronic transformer and incandescent lamps).

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting system. Mixed operation possible in a single circuit. Without additional data line. The module is available for installation inside a luminaire or, with special fixing plate, for external installation. Max. distance luminaire / 2L CG-S: 500 m

Permissible temperature range:

-10°C up to +50°C

Lamp:

- for 4-150 W

Voltage: 230 V 50/60 Hz, 220 V DC +25/-20 %

Loop terminals: 2.5 mm2

Dimensions (mm): H = 27.5; L = 140; W = 39

Degree of protection: IP 20

Accessories:

- Mounting plate with pull-relief

Dimensions (mm): L = 300, W = 50

Type: 2L CG-S

Manufactured by: CEAG