SL/RZ 51011 CG-S

Pos. ...)  ... pcs.

Emergency Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Luminaire with three-sided light emission surface, made of: quick mounting set, body of luminaire with EVG (automatic cut-off for failures within the lamp circuit), clear cover with three self-adhesive legend foils. Luminaire enclosure made of 850°C glow wire resistant, halogen-free polycarbonate. Mounting without tools onto the quick mounting set.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: single-sided with legend foil

Viewing distance: 17 m

As Emergency Luminaire without legend foil:

Max. spacing between luminaire/luminaire and clear cover= 12.2 m

(mounting height = 4 m, C0 level, Emin = 1.25 lx, (luminous flux at the end of the rated duration)

Voltage range: 230 V 50/60 Hz, 220 V DC  +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II, Degree of protection: IP 41

Colour of enclosure: RAL 7035

Inclusive lamp: 8 W T16, 450 lm

Dimensions (mm): L = 342, H = 95, D = 59.5

Type: STYLE SL/RZ 51011 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wall bracket with quick mounting set

- Chain fastening clip incl. quick mounting set

- Pendulum set with wall bracket/termination box and quick mounting set

- Pendulum set IP 54 with quick mounting set

- IP 54 Set

Manufactured by: CEAG

RZ 51021 CG-S

Pos. ...)  ... pcs.

Exit Luminaire acc. EN 60598-1, EN 60598-2-22 and EN 1838.

Luminaire with three-sided light emission surface, made of: quick mounting set, body of luminaire with EVG (automatic cut-off for failures within the lamp circuit), clear, high cover with four self-adhesive legend foils. Luminaire enclosure made of 850°C glow wire resistant, halogen-free polycarbonate. Mounting without tools onto the quick mounting set.

EVG with ENEC-test mark, certified from an independent testing lab, with integrated monitoring facility. Allows single luminaire monitoring with address-switches for 20 addresses.

Switching modes (maintained/non-maintained and switched emergency luminaries) freely programmable with suitable emergency lighting systems. Mixed operation possible in a single circuit.

Marking: three-sided with self-adhesive legend foils

Viewing distance: 17 m

Voltage range: 230 V 50/60 Hz, 220 V DC  +25/-20%

Current drawn (battery operation): 30 mA

Power consumption: 16 VA

Permissible temperature range: -10°C up to +40°C

Loop terminals: 3 x 2.5 sqmm

Insulation class: II, Degree of protection: IP 41

Colour of enclosure: RAL 7035

Inclusive lamp: 8 W T16, 450 lm

Dimensions (mm): L = 342, H = 95, D = 124.5

Type: STYLE RZ 51021 CG-S

Manufactured by: CEAG

Pos. ...)  ... pcs.

Accessories:

- Wall bracket with quick mounting set

- Chain fastening clip incl. quick mounting set

- Pendulum set with wall bracket/termination box and quick mounting set

- Pendulum set IP 54 with quick mounting set

- IP 54 Set

Manufactured by: CEAG