GuideLed  10811 1-8h/D CGLine – for wall surface-mounting parallel to wall

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wall surface-mounting, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of only 40mm including pictogram and mounting set.

Tool-free mounting of LED pictogram to the mounting set. Cable infeeds at rear, above and on side for mains and bus line, with additional space for cable routing.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				100% at 1 h, 80% at 3 h, 25% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		4.8 VA / 4.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 13

Dimensions including wall mounting set:  	W = 226, H = 134,  D = 40

Type: GuideLed 10811 1-8h/D CGLine for wall surface-mounting parallel to wall

Manufacturer: CEAG

GuideLed  10812 1-8h/D CGLine – for semi-recessed mounting parallel to wall

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for semi-recessed mounting in walls, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of pictogram of only 14mm.

Wall recessing housing for cavity walls, for accommodation of supply electronics and battery.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

Can be optionally switched off with reminder of due duration test after 12 months.

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				100% at 1 h, 80% at 3 h, 25% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		4.8 VA / 4.1 W

Insulation class: 				I

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 13

Dimensions of wall recessing housing (mm):	W = 241, H = 112,  D = 40

Wall cut-out 187 x 90

Type: GuideLed 10812 1-8h/D CGLine for semi-recessed mounting parallel to wall

Manufacturer: CEAG

GuideLed  10821 1-8h/D  CGLine – for ceiling surface-mounting

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling surface-mounting, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of ceiling mounting set (mm):	W = 226, H = 33,  D = 80

Type: GuideLed 10821 1-8h/D CGLine for ceiling surface-mounting

Manufacturer: CEAG

GuideLed  10822 1-8h/D CGLine – for suspended mounting, 0.5 m

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for suspended mounting (0.5m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of ceiling mounting set (mm): 	W = 226, H = 33,  D = 80

Type: GuideLed 10822 1-8h/D CGLine for suspended mounting, 0.5 m

Manufacturer: CEAG

GuideLed  10823 1-8h/D CGLine – for suspended mounting, 1.5 m

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for suspended mounting (1.5 m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of ceiling mounting set (mm): 	W = 226, H = 33,  D = 80

Type: GuideLed 10823 1-8h/D CGLine for suspended mounting, 1.5 m

Manufacturer: CEAG

GuideLed  10824 1-8h/D CGLine – for ceiling recessing

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling recessing, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and only 55mm recess depth.

Ceiling recessing housing of sheet steel with steplessly adjustable fixing clips, clamping range 1 to 25 mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of recess housing (mm):  		W = 274, H = 65,   D = 92 (recess depth 61 mm)

Ceiling cut-out (265 mm x 78 mm)

Type: GuideLed 10824 1-8h/D CGLine for ceiling recessing

Manufacturer: CEAG

GuideLed  10825 1-8h/D CGLine – for wire suspension with canopy

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Wire mounting set includes transparent insulated wire suspension for voltage supply.

Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of ceiling mounting set (mm):	W = 226, H = 33,  D = 80

Type: GuideLed 10825 1-8h/D CGLine for wire suspension with canopy

Manufacturer: CEAG

GuideLed  10826 1-8h/D CGLine – for wire suspension and ceiling recessing of supply device

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm. Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m, and freely positionable housing in the ceiling for LED converter, with cable strain relief on primary and secondary side.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				20 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134,  D = 12

Dimensions of module housing (mm):	  	W= 340, W = 50,  H = 46  (angular construction)

Type: GuideLed 10826 1-8h/D CGLine for wire suspension and ceiling recessing of supply device

Manufacturer: CEAG

GuideLed  11811 1-8h/D CGLine – for wall surface-mounting parallel to wall

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wall surface-mounting, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of only 40mm including pictogram and mounting set.

Tool-free mounting of LED pictogram to the mounting set. Cable infeeds at rear, above and on side for mains and bus line, with additional space for cable routing.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		5.3VA / 4.7 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 13

Dimensions including wall mounting set:  	W = 327, H = 184,  D = 40

Type: GuideLed 11811 1-8h/D CGLine for wall surface-mounting parallel to wall

Manufacturer: CEAG

GuideLed  11812 1-8h/D CGLine – for semi-recessed mounting parallel to wall

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for semi-recessed mounting in walls, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low construction height of pictogram of only 14mm.

Wall recessing housing for cavity walls, for accommodation of supply electronics and battery.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				100% at 1 h, 50% at 3 h, 15% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA, coated sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		5.3VA / 4.7 W

Insulation class: 				I

Protection rating: 				IP 20

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 13

Dimensions of wall recessing housing (mm):	W = 292, H = 112,  D = 40

Wall cut-out 187 x 90

Type: GuideLed 11812 1-8h/D CGLine for semi-recessed mounting parallel to wall

Manufacturer: CEAG

GuideLed  11821 1-8h/D  CGLine – for ceiling surface-mounting

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling surface-mounting, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of ceiling mounting set (mm):	W = 327, H = 33,  D = 80

Type: GuideLed 11821 1-8h/D CGLine for ceiling surface-mounting

Manufacturer: CEAG

GuideLed  11822 1-8h/D CGLine – for suspended mounting, 0.5 m

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for suspended mounting (0.5m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of ceiling mounting set (mm):  	W = 327, H = 33,  D = 80

Type: GuideLed 11822 1-8h/D CGLine for suspended mounting, 0.5 m

Manufacturer: CEAG

GuideLed  11823 1-8h/D CGLine – for suspended mounting, 1.5 m

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for suspended mounting (1.5 m), according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of ceiling mounting set (mm):  	W = 327, H = 33,  D = 80

Type: GuideLed 11823 1-8h/D CGLine for suspended mounting, 1.5 m

Manufacturer: CEAG

GuideLed  11824 1-8h/D CGLine – for ceiling recessing

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for ceiling recessing, according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm. Ceiling recessing housing of sheet steel with steplessly adjustable fixing clips, clamping range 1 to 25 mm.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of recess housing (mm):  		W = 374, H = 65,   D = 92 (recess depth 61 mm)

Ceiling cut-out (365 mm x 78 mm)

Type: GuideLed 11824 1-8h/D CGLine for ceiling recessing

Manufacturer: CEAG

GuideLed  11825 1-8h/D CGLine – for wire suspension with canopy

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Wire mounting set includes transparent insulated wire suspension for voltage supply.

Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of ceiling mounting set (mm):  	W = 327, H = 33,  D = 80

Type: GuideLed 11825 1-8h/D CGLine for wire suspension with canopy

Manufacturer: CEAG

GuideLed  11826 1-8h/D CGLine – for wire suspension and ceiling recessing of supply device

Pos.    )		ea.

Self-monitoring LED self contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-718 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

An additional non-shielded 2-core bus line to the luminaires is required when connected to the central monitoring facility CG-Controller CGLine 400 or CGLine WEB-Interface.

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram, uniformity Lmin/Lmax > 0.8.

High service life via optimised LED operating conditions.

Increased safety via redundant construction of LED unit consisting of 3-chip LEDs with high luminous efficacy >100 lm/W for significantly reduced connected load.

Polarity reversal-protected wiring of LED unit.

Slender design with low pictogram width of only 12mm. Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m, and freely positionable housing in the ceiling for LED converter, with cable strain relief on primary and secondary side.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED.

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

(according to DIN VDE 0100-718)

- Blocking function via CG-Controller CGLine 400 or CGLine WEB-Interface during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N: 				single-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

double-sided: 85% at 1 h, 25% at 3 h, 8% at 8h

Emergency light rated operating time:		1 h, 3 h or 8 h

Battery						LiIon 3.7V 2000 mAh

Recognition distance: 				30 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Plug-in terminal 4 x 2 x 2.5 mm² (mains connection)

CGLine bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50 Hz

Connected load with mains operation:		single-sided 5.3VA / 4.7 W

double-sided 6.6 VA / 6.3 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 327, H = 184,  D = 12

Dimensions of module housing (mm):		W= 340, W = 50,  H = 46  (angular construction)

Type: GuideLed 11826 1-8h/D CGLine for wire suspension and ceiling recessing of supply device

Manufacturer: CEAG